## OASIS
(Transmission lines rated 138kV and higher that limit bulk power transfers are listed)
Nova Scotia Power |  |  |  | For help, contact: |  |  |  |  | FIM (Flow into Metro) |  | Last Update: | Legend
Transmission Operations |  |  |  | nspsoadmin@nspower.ca | [6 empty] | 2025-08-01 12:00 | Please note all Planned Outages in Green indicates new updates
Transmission Planned Outage Schedule
Circuit/Element | For Work On | Start Date | Return Date | Reason | CBX | ONI | ONS | EEX@EB | MDRR | FIM | Generation Restrictions | Import/Export | Notes | Work Status
L-8002 | L-8002 | 7/15/2025 | 8/14/2025 | Maintenance | [6 empty] | MINIMUM TUFTS COVE GENERATION BASED ON LOAD: GROSS GENERATION = 0.4047*(NET SYSTEM LOAD) - 360.54 | ONS<= 770 MWs ONI<= 1275 MWs | Line will be in service every FRIDAY SATURDAY and SUNDAY for the duration of the Outage
Maritime Link | Maritime Link | 7/31/2025 0800 | 7/31/2025 1200 | Testing | [7 empty] | ML Restricted to 175MWs at Bottom Brook
TL211 Outage | TL211 Outage | 8/5/2025 10:00 | 8/15/2025 1600 | NFL Mtce | [7 empty] | ML <=250 MW
L-8001 | L-8001 | 8/5/2025 12:00 PM | 8/5/2025 15:00 PM | Maintenance | [6 empty] | (NB to NS + NS MSSC) limited to 250 MW, therefore: (NB to NS) + (LG3+LG4) limited to 250 MW (NB to NS) + (TR5+TR6) limited to 300 MW (NB to NS) + ML limited to 250 MW (NS to NB) + (NS Max Load Loss) limited to 220 MW | NB to NS is limited to 100 MW NS to NB is limited to 140 MW NB to (NS+PEI) limited to 300 MW
L-6613 | 1N-613 | 6/8/2025 | 7/8/2025 | Maintenance | [7 empty] | NB Exports Limited to 330MW NB Imports limited to 305MW and not to exceed 27% of Net System load (Normal).
NB STOP 014 | NB STOP 014 | 8/7/2025 | 8/8/2025 | Maintenance | [7 empty] | #VALUE!
LIL POLE 1 OUTAGE | LIL POLE 1 OUTAGE | 9/14/2025 | 9/20/2025
ML POLE 1 OUTAGE | ML POLE 1 OUTAGE | 9/15/2025 | 9/19/2025
ML POLE 2 OUTAGE | ML POLE 2 OUTAGE | 9/19/2025 | 9/22/2025
LIL BIPOLE OUTAGE | LIL BIPOLE OUTAGE | 9/21/2025 | 9/30/2025
LIL POLE 2 OUTAGE | LIL POLE 2 OUTAGE | 10/1/2025 | 10/14/2025