## OASIS
(Transmission lines rated 138kV and higher that limit bulk power transfers are listed)
Nova Scotia Power |  |  |  | For help, contact: |  |  |  |  | FIM (Flow into Metro) |  | Last Update: | Legend
Transmission Operations |  |  |  | nspsoadmin@nspower.ca | [6 empty] | 2025-10-30 13:00 | Please note all Planned Outages in Green indicates new updates
Transmission Planned Outage Schedule
Circuit/Element | For Work On | Start Date | Return Date | Reason | CBX | ONI | ONS | EEX@EB | MDRR | FIM | Generation Restrictions | Import/Export | Notes | Work Status
NB STOP 023 | NB STOP 023 | 10/27/2025 | 10/31/2025 | [8 empty] | Limit flows to NS + PEI to 300MW
L-7003 + L-6613 | L-7003 + L-6613 | 10/28/2025 | 10/30/2025 | Dynamic Line Rating Sensor Installation | [7 empty] | Cape Breton Export is limited to 940 MW Onslow Import is limited to 1120 MW NB TO NS IMPORT <= 50MW NS TO NB EXPORT <=300MW
L-7003 | L-7003 | 10/31/2025 | 2025-11-01 | Dynamic Line Rating Sensor Installation | [7 empty] | Cape Breton Export is limited to 985 MW Onslow Import is limited to 1180 MW
L-7004 | L-7004 | 11/02/2025 | 11/02/2025 | Dynamic Line Rating Sensor Installation | [7 empty] | Cape Breton Export is limited to 980 MW Onslow Import is limited to 1215 MW
L-8001 | L-8001 | 11/02/2025 0700 | 11/02/2025 1100 | Dynamic Line Rating Sensor Installation | [7 empty] | Onslow Import is restricted to 1150 MW Cape Breton Export is restricted to 1150 MW • NB to NS is limited to 100MW. • NS to NB is limited to 140 MW. • Limit NB to (NS+PEI) to 300MW. | With 0 MW NB TO NS: TR5 + TR6 = 300MW LIN3 + LIN 4 = 250MW ML <= 250MW
L-7004 + L-6613 | L-7004 + L-6613 | 11/03/2025 | 11/04/2025 | Dynamic Line Rating Sensor Installation | [7 empty] | Cape Breton Export is limited to 940 MW Onslow Import is limited to 1120 MW NB TO NS IMPORT <= 50MW NS TO NB EXPORT <=300MW
L-8002 | L-8002 | 11/03/2025 | 11/06/2025 | [8 empty] | MINIMUM TUFTS COVE GENERATION BASED ON LOAD: GROSS GENERATION = 0.4047*(NET SYSTEM LOAD) - 360.54 | ONS<= 770 MWs ONI<= 1275 MWs
ML POLE 2 | ML POLE 2 | 11/10/2025 8AM | 11/10/2025 1500 | [8 empty] | ML<=250 MW