## OASIS
(Transmission lines rated 138kV and higher that limit bulk power transfers are listed)
Nova Scotia Power |  |  |  | For help, contact: |  |  |  |  | FIM (Flow into Metro) |  | Last Update: | Legend
Transmission Operations |  |  |  | nspsoadmin@nspower.ca | [6 empty] | 2026-06-17 16:00 | Please note all Planned Outages in Green indicates new updates
Transmission Planned Outage Schedule
Circuit/Element | For Work On | Start Date | Return Date | Reason | CBX | ONI | ONS | EEX@EB | MDRR | FIM | Generation Restrictions | Import/Export | Notes | Work Status
91H-T11 | 91H-T11 | 3/24/2026 | 7/17/2026 | [7 empty] | TC2 must run at Basic System Loads >1500 MW
L-6539 | L-6539 | 6/08/2026 | 7/14/2026 | [7 empty] | Wreck cove Generation limited to 190MW, Lingan (each unit) Generation limited to 160MW
L-8002 | L-8002 | 2026-06-15 | 2026-06-18 | [7 empty] | Minimum TC Generation (Gross) = 0.4519 * (Basic system load)- 374.19 | ONS limited to 670MW ONI limited to 1200MW CBX limited to 940MW Flow Into Metro Limited to 350MW
NB STOP 002 | NB STOP 002 | 6/15/2026 | 6/24/2026
NB STOP 003 | NB STOP 003 | 6/18/2026 | 6/19/2026 | [7 empty] | LIMIT FLOWS (NS + PEI) TO 300MW MAX OVER ALL SYSTEM LOADS
LIL BIPOLE OUTAGE | LIL BIPOLE OUTAGE | 6/21/2026 | 6/25/2026
NB STOP 004 | NB STOP 004 | 2026-06-22 | 2026-06-22 | [7 empty] | #VALUE!
L-7004 | L-7004 | 6/22/2026 | 6/25/2026 | [8 empty] | CBX: LIMITED TO 820MW ONI: LIMITED TO 940MW
ML POLE 2 OUTAGE | ML POLE 2 OUTAGE | 6/23/2026 0600 | 6/25/2026 1700 | [8 empty] | ML <= 250 MWs | if ML > 168 MWs then {10 min Reserve Requirement = Flows on ML} Else if ML <= 168 MWs {10min Reserve Requirement = 168MWs}
LIL SOFTWARE DYNAMIC COMMISSIONING |  | 6/25/2026 0730 | 7/4/2026 1700