## OASIS
(Transmission lines rated 138kV and higher that limit bulk power transfers are listed)
Nova Scotia Power |  |  |  | For help, contact: |  |  |  |  | FIM (Flow into Metro) |  | Last Update: | Legend
Transmission Operations |  |  |  | nspsoadmin@nspower.ca | [6 empty] | 2026-07-15 10:30 | Please note all Planned Outages in Green indicates new updates
Transmission Planned Outage Schedule
Circuit/Element | For Work On | Start Date | Return Date | Reason | CBX | ONI | ONS | EEX@EB | MDRR | FIM | Generation Restrictions | Import/Export | Notes | Work Status
91H-T11 | 91H-T11 | 3/24/2026 | 7/28/2026 | [7 empty] | TC2 must run at Basic System Loads >1500 MW
50W-615 | 50W-615 | 6/22/2026 | 7/31/2026 | [7 empty] | Tusket CT is available for generation
L-6539 | L-6539 | 7/16/2026 | 7/30/2026 | [7 empty] | 1 WC must be available Wreck cove Generation limited to 190MW, Lingan (each unit) Generation limited to 160MW
L-6005/L6010 | L-6005/L6010 | 7/16/2026 | 7/17/2026 1800 | [7 empty] | Minimum Metro Generation = 0.613 * (Basic system load) - 606.12 |  | Metro Generation consists of Tufts cove, Burnside CTs, and the Spider Lake BESS
L-5003 | L-5003 | 7/20/2026 6:00:00 AM | 7/20/2026 4:00:00 PM | [7 empty] | TC2 must be online
LIL POLE 1 OUTAGE | LIL POLE 1 OUTAGE | 7/23/2026 8:00:00 AM | 7/23/2026 4:00:00 PM | [9 empty] | If ML > 168 MWs then {10 min Reserve Requirement = Flows on ML} Else if ML <= 168 MWs {10min Reserve Requirement = 168MWs}
LIL POLE 2 OUTAGE | LIL POLE 2 OUTAGE | 7/24/2026 8:00:00 AM | 7/24/2026 4:00:00 PM | [9 empty] | If ML > 168 MWs then {10 min Reserve Requirement = Flows on ML} Else if ML <= 168 MWs {10min Reserve Requirement = 168MWs}